## Slide 1
TOWARDS THE DESIGN OF RESILIENT AND SAFE
NUCLEAR SYSTEM WITH IMPRECISE PROBABILITY
Centre for intelligent infrastructure
Civil and Environmental Engineering
Edoardo PATELLI, Enrique MIRALLES DOLZ, Ander GRAY, T.V. SANTHOSH
4th International Seminar on Probabilistic Methodologies for Nuclear Applications 1-3 November 2022 Leicester, UK

## Slide 2: Nuclear power plant
Methodologies, licensing, and regulation of "matured" engineering systems are well established

## Slide 3: Next generation plants
HTGR demonstration programme

## Slide 4: Digital Reactor Design Not a digital twin, yet
It is a fusion of models and data that evolves over time
Challenges
Output Accuracy Estimation
Computational Costs
Software Integration
Our contributions
Uncertainty Propagation Sensitivity Analysis
Reliability Analysis
Notes: 4

## Slide 5: The data problem Data overflow and data shadowing
Data availability is expect to increase
Cheap sensors, tracking and logs, surveillance
Are the data relevant?
Are we measuring the right thing?
Machine learning and AI should support uncertainty characterisation
Data robustness and trustfulness
Data tempering and malicious injection of false data

## Slide 6: The knowledge problem Engineering shadowing
Know your limits
A digital twin will never be a perfect replica of the physical world
Digital twins to support the understanding of engineering problem (Explainability, Transparency and Provability)
Uncertainty propagation should be an embedded feature in the digital twin and UQ a by-product
Lack of standard, legal framework and old technology
Notes: Capacity to be demonstrated

## Slide 7: Towards safe and resilient systems
This Photo by Unknown Author is licensed under CC BY-NC-ND

## Slide 8: … from risk-led to resilience-led
With too many risks and complexity of modern systems we should be focused on consequences rather than causes.
Traditional, quantitative, probabilistic, approach to risk is no longer valid for modern times
“There is a strong argument for moving from a risk to a resilience-based model”

## Slide 9: Robustness for improved safety
Avoiding things that go wrong (Erik Hollnagel)
Part of the “Defense in Depth”
Safety margin*
Design-basis accident and worst-case credible accident*
Fragility analysis**
Probability safety assessment
* Does not include quantification of the probability ** Decoupling system response from the hazard
What about unknown unknowns?

## Slide 10: Resilience engineering
It is the characteristic of being able to adapt under stress or faults in order to avoid failure
Absorbed (anticipate)
Mitigate (monitor)
Recovery (respond)
Adapt (learn)
Credit David Woods
Changes focus from the negative to the positive attributes

## Slide 11: Measuring resilience
Which performance to use?
“Safety” vs “productivity”
Digital twin

## Slide 12: Everything is resilient
Collapsed 14 August 2018, Reopen to the traffic on the 4 August 2020

## Slide 13: Measuring Resilience
PSA: probability of the threats X consequences.
Resilience: capability of the system to recover the system
Resulting performance states
Which path do we need to consider?
Notes: The system is designed to remove the heat generated in the calandria due to fission reaction in a typical nuclear reactor. The pumps take suction from the calandria and deliver back to the calandria through a set of heat exchangers and isolation valves.
For the successful operation of the system, at least two out of three pumps and heat exchangers with associated valves are needed to ensure continuous heat removal.
Reliability doesn’t consider the dynamic repair aspects unlike resilience which has significant effect on overall performance.
As the resilience strongly depends on many factors including human and organisational factors, the recovery time is proportional to the decision making and task execution.

## Slide 14: Measuring Resilience with safety
Safety level depends on the number of remaining safety measures to manage the disruptive event (e.g. auto setback function, manual setback function and a complete shutdown recovery)
Resilience can be measured as the number of possible recovery paths (options) that are still available to recover the system.
Notes: The system is designed to remove the heat generated in the calandria due to fission reaction in a typical nuclear reactor. The pumps take suction from the calandria and deliver back to the calandria through a set of heat exchangers and isolation valves.
For the successful operation of the system, at least two out of three pumps and heat exchangers with associated valves are needed to ensure continuous heat removal.
Reliability doesn’t consider the dynamic repair aspects unlike resilience which has significant effect on overall performance.
As the resilience strongly depends on many factors including human and organisational factors, the recovery time is proportional to the decision making and task execution.

## Slide 15: Integrated resilient metric
Safety measure resilience factor
Resilience of each recovery sequence
Total resilience
probability success of the ith safety measure’ l: available safety measures during restoration; k: number safety measures available before the disruptive event; probability of the total safety measures
: performance function; : resilience to safety-resilience weighing factor
Notes: The system is designed to remove the heat generated in the calandria due to fission reaction in a typical nuclear reactor. The pumps take suction from the calandria and deliver back to the calandria through a set of heat exchangers and isolation valves.
For the successful operation of the system, at least two out of three pumps and heat exchangers with associated valves are needed to ensure continuous heat removal.
Reliability doesn’t consider the dynamic repair aspects unlike resilience which has significant effect on overall performance.
As the resilience strongly depends on many factors including human and organisational factors, the recovery time is proportional to the decision making and task execution.

## Slide 16: Case study advanced nuclear reactor
Regulating system
  4 regulating rods
  4 shim rods
  8 absorber rods
Primary shutdown system
12 mechanical rods (similar to shim rods)
Secondary shutdown system
12 tubes with liquid poison
A threat causing failure of one of the control rods
Regulation system is expected to recover from either auto setback recovery or by manual setback
Notes: Geometric mean of all the recovery sequences with associated weightage for each successful recovery.

## Slide 17: Recovery model and human factor
Human factors
RRS
Threat
Initial system state
Threat detection
Actuate auto recovery
Actuate manual recovery
New system state
Shim rods
Operator intervention
Human & organizational factors
Control rods
Sensing mechanism
Emergency shutdown
Restart system
Damage state
Shutdown systems
Yes
Yes
Yes
No
No
No
No
Yes
No
Notes: Geometric mean of all the recovery sequences with associated weightage for each successful recovery.

## Slide 18: Petri net model
18
Macchiato software
by University of Nottingham
Human factor model
Shutdown recovery model
Manual recovery model
Auto recovery model
Control rod model
Threat simulation
Notes: Geometric mean of all the recovery sequences with associated weightage for each successful recovery.

## Slide 19: Selected results
Practically impossible to compute manually the resilience for each successful sequence
The recovery time obtained from the Petri net model
106 simulation performed
Safety measures | Performance (availability) |  |  | Sequence resilience | weightage | Performance-based Global resilience |  | Safety-based sequence resilience | Safety-based Global resilience
 | Initial | Disruptive | Recovery |  |  |  |  |  | 
Auto | 100 | 93.4 | 98.9 | 0.83 | 0.99 | 0.81 | 1.0 | 0.83 | 0.66
Manual | 100 | 89 | 98.9 | 0.9 | 0.89 |  | 0.67 | 0.603 | 
Safety measures | Performance (availability) |  |  | Sequence resilience | weightage | Performance-based Global resilience |  | Safety-based sequence resilience | Safety-based Global resilience
 | Initial | Disruptive | Recovery |  |  |  |  |  | 
Auto | 100 | 93.4 | 98.9 | 0.83 | 0.99 | 0.81 | 1.0 | 0.83 | 0.66
Manual | 100 | 89 | 98.9 | 0.9 | 0.89 |  | 0.67 | 0.603 | 
Notes: Geometric mean of all the recovery sequences with associated weightage for each successful recovery.

## Slide 20: Resilience and data
Learning from adversity and becoming better able to avoid and manage future stresses
Resilience Engineering requires a lot of data and data analytics for real-time analysis, state identification and prognostic, automatic decision making

## Slide 21: Dealing with imprecision

## Slide 22: Aleatory vs Epistemic uncertainty
Variability vs. Imprecision
Epistemic uncertainty is the “controllable” uncertainty
Aleatory uncertainty is the remaining uncertainty after As Low As Reasonable Archivable (ALARA) campaign is performed to characterise the uncertainty
Epistemic uncertainty measures the error from the modelled uncertainty to the ”true” uncertainty Joshua Kaizer (US Nuclear Regulatory Commission)
In principle, probability theory can describe both (some say) but it mixes and confuses observed data and subjective belief

## Slide 23: Imprecise probability
Model incertitude as a set of possible values
Interval analysis and Fuzzy variable
Modelling epistemic uncertainty
Dempster-Shafer structure
Different probability masses associated to distinct intervals
Probability boxes
Combine aleatory and epistemic uncertainty
x
p1
p2
p3

## Slide 24: Computing with confidence
Suppose A is in [2,4] and B is in [3,5] What about the sum A+B?
The right answer is [5,9]
Including confidence intervals
  1/10 is different than 100/1000
  No observations is different than 0 probability

## Slide 25: Computational challenges
Patelli, E., Alvarez, D.A., Broggi, M., de Angelis, M., 2015. Uncertainty management in multidisciplinary design of critical safety systems. J. of Aerospace Information Systems 12, 140–169 https://doi.org/10.2514/1.I010273
Propagate uncertainty and incertitude without mixing/confusing

## Slide 26: Computing with imprecise probabilities

## Slide 27: Computational tools
ProbabilityBoundsAnalysis.jl
MomentArithmetic.jl
ZoneArithmetic.jl
(p-box arithmetic)
Probability Theory
Interval Arithmetic
(moment arithmetic)
(Subintevalization)

## Slide 29: Intervals

## Slide 30: Intervals

## Slide 31: Probability boxes

## Slide 32: Probability boxes

## Slide 33: Probability boxes

## Slide 34: Probability boxes
More precision
Less stochasticity

## Slide 35: Distributions with imprecise parameters
Normal
Uniform
Beta
Lognormal
Gamma
Exponential
Chi squared
Cauchy

## Slide 36
Binary operations

## Slide 37: What if we do not have a distribution?

## Slide 38: First order error propagation
In probability theory called “Moment propagation”
Propagates mean & variance through mathematical expressions
Although widely used, requires a lot of assumptions, and does not inform about distribution shape
    Requires stochastic independence
    Moments must be perfectly known
    Gives no information about tails without distribution assumption
    Only accurate for near-linear models
        Bad for risk analysis
Pessimism from Cullen and Frey (1999)

## Slide 39: Moment arithmetic
Generalisation with the following:
        Independence between variables need not be assumed
        Moment propagation formulae may be evaluated with intervals
        Assumptions about input distributions is no longer necessary
        Works for non-linear functions
Computer arithmetic on random variable’s range, mean and variance
7 binary operations: +, -, *, /, ^, min, max
9 unary operations: rescale, shift, exp, log, ln, 1/x, , ,
For independence and unknown dependence (Fréchet)
https://doi.org/10.1016/j.ijar.2022.04.001

## Slide 40: Moment arithmetic
Yields intervals
Arithmetic with independence
Arithmetic without dependence assumptions (Fréchet)
Interval arithmetic
Rigorous formulas for least and greatest possible values

## Slide 41: Compute with missing information
Mean and variance bounded from ranges
Tighter variance when mean is given
Given mean is too wide
Inconsistent mean
Inconsistent variance
Mean and variance bounds can be estimated from range

## Slide 42: Bounds of CDF

## Slide 43: Arithmetic tables with intervals
Even starting with point estimates for means and variances, the moment arithmetic tables formulas generally yields interval results.
EX, VX, and bounds can be intervals
Repeated variables
Subintervalisation: interval calculations
Since only 2 variables are intervals, subintervalisation works well

## Slide 44: Dependent variables
Even if X and Y are non-dependent, Z and X are dependent
Y
X
Z

## Slide 45: Zone arithmetic
X
Y
X
Z
      https://github.com/AnderGray/ZoneArithmetic.jl

## Slide 46: Tracking dependencies
Dependencies can be tracked in a graph
The nodes are variables (intervals)
The edges are dependencies (zones)
When a new variable is calculated, it’s added and linked in the graph
A
B
C
D
E

## Slide 47: Dependence tracking

## Slide 48: Dependence tracking with subintervals

## Slide 49: Compute risk with missing information
If the mean is 10 and the variance is 2, best-possible bounds on the chance the variable is bigger than any value is given by this p-box.
-10
0
10
20
30
0
Exceedance risk
1
Prob(15 < X)  [0, 0.08]
The chance that a normal random variable with mean 10 and variance 2 is bigger than 15 is only 0.000203

## Slide 50: Risk analysis
Independence (of events) is often assumed it can have dramatic consequences.
https://doi.org/10.1007/978-3-031-08971-8_64

## Slide 51: What if we only have a black box?

## Slide 52: Advanced Monte Carlo methods Rare event simulation
Efficient approached able to deal with imprecision
Advanced line sampling
Subset simulation
Sequential Monte Carlo based algorithm
de Angelis, M., Patelli, E., Beer, M., 2015. Advanced line sampling for efficient robust reliability analysis. Structural safety 52, 170–182. https://doi.org/10.1016/j.strusafe.2014.10.002
Au, S.K., Patelli, E., 2016. Subset Simulation in finite-infinite dimensional space. Reliability Engineering & System safety 148, 66–77. https://doi.org/10.1016/j.ress.2015.11.012
Lye, Adolphus, Alice Cicirello, and Edoardo Patelli. ‘Advanced Sampling Methods for Solving Bayesian Model Updating Problems: A Tutorial’. Mechanical Systems and Signal Processing 159 (2021): 107760. https://doi.org/10.1016/j.ymssp.2021.107760.
Notes: 52

## Slide 53: Computing with confidence Dealing with uncertainty in digital twins
Reliable and robust surrogate models Interval predictor models / Interval Neural Network
Regression models which predict an interval with a confidence level
Trained with minibatch gradient descent in TensorFlow, cost O(minibatch size)
Works with imprecise training data
Sadeghi, J., Angelis, M. de, Patelli, E., 2019. Efficient training of interval Neural Networks for imprecise training data. Neural Networks 118, 338–351. https://doi.org/10.1016/j.neunet.2019.07.005
Notes: Therefore we need robust algorithms and computational methods able to deal with uncertainty. This is one of the my main area of research: dealing with uncertainty.
Developing robust and reliable computational tools able to deal with different representation of the uncertainty from bad data, expert elicitation till no data.
These tools in turns allow to construct what is called a credible digital replica of our infrastructure that using data from sensors and prior knowledge of the systems allows to monitor and control the behaviour of structures and systems, providing adaptation capability. However this can only be done if the uncertainties and the unknowns are taken explicitly into account and their effects are quantified.
Reliable and efficient approaches are also needed to reduce the computational cost of the analysis making the computational task sustainable. Robust techniques that require very few assumptions has been developed including interval neural networks and robust Bayesian neural networks.

## Slide 54: Summary
Imprecise probability allows to deal with lack of knowledge and imprecision without unjustified assumptions
Rigorous propagation of uncertainty exist (intrusive and non-intrusive) and freely available libraries
Resilience is an additional metric but allows to handle unknowns

## Slide 55
X THE PLACE OF USEFUL LEARNING
Contacts: Edoardo Patelli
Edoardo.patelli@strath.ac.uk
#EdoardoPatelli
www.cossan.co.uk
Acknowledgment: Scott Ferson