## Slide 1: Assessing Passive Components with Risk-Informed Thinking
David L. Rudland Senior Technical Advisor for Materials Office of Nuclear Reactor Regulation U.S. Nuclear Regulatory Commission
2022 International Symposium on Probabilistic Methods for Nuclear Applications
Leicester University Space Park, Leicester LE4 5SP UK
November 1-3, 2022

## Slide 2: Risk-informed Decision Making
Objective is integrated decision making
Key is risk informed not risk based
Use of risk insights for passive component integrity – How to assess components not modelled in PRA?
Can PFM be used for regulatory discussions outside of RIDM?
Integrated Decision Making
Defense-in-depth
Safety Margins
Increase in risk or CDF is small
Monitoring
Change meets current regulation
2

## Slide 3: Use of Probabilistic Fracture Mechanics
3
Probabilistic Fracture Mechanics (PFM) is being used
Requests for Inspection Relief
LOCA Frequencies
LBB
Others?
Formalized review process for risk-informed decision making
No Formalized review process for risk-informed decision making – Should we follow similar process??

## Slide 4: Risk-Informed Licensing
Other licensing actions
Guidance/
Process
needed
Where are the passive component integrity assessments?
4

## Slide 5: Licensing Reviews and Emergent Issues
Risk/PRA
Acceptability
Risk information
submitted outside of the formal risk-informed licensing basis change process
Reliance on Licensee Risk Information
Qualitative
Quantitative
Deterministic
Reviews
Relief Requests
Requests with PFM
Process under development
LIC-206, others
Process defined
Emergent issues?
Process defined
LIC-504
Risk-Informed
License Basis
Changes
(RD 1.174/RG 1.200
TSTF-505 Risk-informed
Completion times
NFPA-805 Risk-informed
Fire Protection
10CFR 50.69
SSC Categorization
5b Risk-informed
Surveillance Frequencies
Risk-informed
Inservice Inspection
Need adequate, consistent information and confidence in results
5

## Slide 6: Past Applications of PFM
Biggest Major Program successes:
  Risk-informed Inspection for Piping
  Elimination of BWR reactor pressure vessel circumferential weld inspections
  Pressurized thermal shock analysis for reactor pressure vessel
Reasons for success
  Computer code bases were technically adequate (V&V) – staff was able to fully review code or had similar code for confirmatory analyses
  All Principles of risk informed decision making were assessed
  In many cases, deterministic and probabilistic analyses were used as basis
  Sensitivity/uncertainty analyses used to demonstrate impact of important variables
6

## Slide 7: Current Applications of PFM
Extending ISI interval to more than 10 years for
  Steam generator
  Pressurizer
  Heat exchangers
Extension to 20 years has been approved in the past
Extension beyond 20 years needs further justification
Some licensee are seeking to delay inspections for remainder of licensed life
7

## Slide 8: Risk-informed Modifications to Inspection
Degradation occurs where the conditions necessary for a particular mechanism exist – typical ISI programs are not focused.
Locations that have a higher failure potential with a significant consequence of that failure (i.e., risk) can be targeted for inspection
NRC uses a risk-informed decision-making methodology to determine impact
But we only know what we learned from operational history
Integrated Decision Making
Defense-in-depth
Safety Margins
Increase in risk or CDF is small
Monitoring
Change meets current regulation
Assessing Passive Components with Risk-Informed Thinking
8

## Slide 9: Using Risk Arguments for Inspections
What if we are wrong?
Additional degradation
Unknown behavior
9

## Slide 10: Operational History
Due to IGSCC
Assessing Passive Components with Risk-Informed Thinking
10
1.5 years/
mechanisms
6 years/mechanisms
Burn-in
Maturity
Wear-out
Chance of failure
The potential for new mechanisms must be considered

## Slide 11: Risk Arguments for ISI
Monitoring
Analysis (PRA, PFM, etc)
Result
Snapshot in time
Real time Results
Probabilistic fracture mechanics and other advanced analytical techniques model the state-of-the-art with the current-day knowledge
Modelling the unknown is always a major question and limitation of these analyses
Monitoring provides the necessary feedback
November 1-3, 2022
11

## Slide 12: How Much Performance Monitoring is Enough?
Many components in US plants are in the “maturity” phase
Examinations are primarily confirming operating experience and monitoring for novel degradation
Strategies such as primary/expansion (MRP-227) or fleet coordination (WCAP-16168) may be adequate to demonstrate performance monitoring
Statistical techniques may be used to define minimum inspection required to find unique degradation
Assessing Passive Components with Risk-Informed Thinking
12

## Slide 13: Binomial Distribution
The binomial distribution is frequently used to model the number of successes in a sample of size n drawn with replacement from a population of size N
Can be used to find # of inspections needed to find a crack
Only a function of the number of inspections and the % cracked
Does not demonstrate the impact of sample size
Very easy to use
k= number of successes (cracks found) , n=number of trials (inspections)
p= probability of success on an individual trial (% of population cracked)
If k=0 then this is the probability of no successes is:
and therefore, the probability of at least one success is
13

## Slide 14: Monte Carlo Analysis
Same idea can be developed through a MC analysis
Allows maximum flexibility in analysis
Binomial response can be recreated
Sample a weld population with x% cracked
Loop on weld population
cracked?
Sample Inspection of y% of welds
inspected?
count=count+1
MC Loop, n realizations
p=count/n
yes
yes
no
no
Done?
yes
no
Done?
yes
no
14
For large populations

## Slide 15: Examples
15
Impact of small sample size
Binomial solution versus time

## Slide 16: Performance Monitoring Program
A modified binomial solution, with time correction, may be sufficient to design a conservative inspection program
Correcting the binomial solution is just a rough approximation and may be non-conservative in the number of inspections needed to find a growing crack
A detailed MC analysis can better define the response, and can model crack growth and inspections directly
Small sample size makes it difficult to define a conservative inspection program
Leveraging other similar materials to expand the weld population should be considered
16

## Slide 17: Risk Informed Materials Assessment
Regulatory guidance providing framework for submitting and reviewing materials engineering applications with Risk informed decision-making (RIDM) aspects
Ambitions
Challenge
Status
Goal
NRC Staff lead project
Existing NRC RIDM guidance focused on use of PRA
RIDM guidance for passive component integrity not available
Handling of uncertainties lacks guidance
Guidance would provide key aspects to include in high-quality submittals as well as the interaction between these key aspects as they may relate to NRC review decisions.
Project officially initiated
NRC staff developing internal draft concepts
Public participation in project is planned
Assessing Passive Components with Risk-Informed Thinking
17

## Slide 18: Summary
Risk-informed decision-making is being used to propose certain changes in requirements for passive components
NRC uses integrated decision making considering the five principles of risk-informed decision making in determining impacts
When modifying inspection intervals using PFM as the basis, performance monitoring provides the necessary feedback to demonstrate continued adequacy of the analyses.
Statistical methods is one option in designing a performance monitoring program
18